## Library! At Hilcrest
Caption: Library! At Hillcrest ADA assessment findings, recommendations for remediation, and associated costs.
ID | LOCATION | BUILT BEFORE ADA | VIOLATIONS | 2010 ADA CODE | RECOMMENDATIONS | ESTIMATED COST | QUICK FIX | PRIORITY SCORE
2672 | Parking | Unknown | There are no marked "Van accessible" spaces. | §208.2.4 | Add a 132" wide van accessible parking space for every six vehicle parking spaces. Add a “van accessible” parking sign at a minimum height of 60" above the ground. | 1000 | No | 2
2609 | Parking | Unknown | The parking spaces closest to Camp Rhino Boise have slopes ranging from 2.6% to 5.4%. The access aisle has a 2.7% slope. | §502.4 | Resurface the parking spaces and access aisle to reduce the slope to a maximum of 2% in all directions. | 3000 | No | 3
2612 | Parking | Unknown | The parking spaces have a 4% to 4.4% slope. The access aisle has a 2.6% slope | §502.4 | Resurface the parking spaces and access aisle to reduce the slope to a maximum of 2% in all directions. | 3000 | No | 3
2615 | Step Ahead Idaho | Unknown | The counter is 42" above the floor and the table is 28.5" above the floor. | §904.4.1 | If necessary, utilize the low table as the lower counter for users with disabilities.A portion of the service counter must be no higher than 36" above the floor for a horizontal distance of 36". | 1000 | No | 4
2633 | Family Restroom | Unknown | The centerline of the toilet is located 19" from the sidewall. | §604.2 | Reposition the centerline of the toilet to be within 16" minimum and 18" maximum from the sidewall. | 1000 | No | 5
2628 | Lemhi Room | Unknown | There is no knee clearance underneath the counter. | §306.3.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. | 1000 | No | 5
2657 | Men’s Restroom | Unknown | The accessible water closet does not have a vertical grab bar. | ICC A117.1 §604.5.1 | The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the real wall.Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. | 1000 | No | 5
2611 | Parking | Unknown | The accessible route passes behind parked vehicles. | Advisory §502.3 | The sidewalk shall be connected to a marked crosswalk to access the library.For the purposes of achieving greater accessibility and Human Centric Design, where possible, it is preferable that a sidewalk be constructed in front of the accessible parking spaces. | 5000 | No | 5
2618 | Step Ahead Idaho Restroom | Unknown | There is no knee clearance underneath the counter. | §306.3.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. | 1000 | No | 5
2666 | Drinking Fountains | Unknown | The spout heights of the drinking fountains are not compliant at 31" and 36.75" above the floor. | §602.7 | Raise the existing tall drinking fountain to a minimum spout height of 38" and maximum spout height of 43" above the floor. | 1000 | No | 6
2670 | Main Entrance | Unknown | The work surface counter is 40" above the floor.There is no knee clearance underneath the counter. | §306.3.3, §902.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor.Lower the work surface counter to a maximum height of 34” above the floor or provide a lower, accessible computer work station. | 2000 | No | 8
2614 | Main Entrance | Unknown | The exit push button is blocked by the sensor wall making it difficult to access the push button when going through the security sensors.At the time of the assessment, the security sensors were not operable. | §308.3.1 | removing or repairing the security sensors.For the purposes of achieving greater accessibility and Human Centric Design, relocate the exit button to before the security sensors on the accessible route and consider | 3000 | No | 8
2669 | Main Entrance Laptop Station | Unknown | The interactive touch screen does not have any sound or tactile components. Therefore, a visually impaired person would not be able to access the information provided by the kiosk. | §707 | Controls to operate the kiosk must meet the requirements of §707.Audio instructions must be provided that guide the user through all the functions of the machine. Tactile instructions must be provided informing the user on the method of activating the audio instructions. | 3000 | No | 8
2625 | Teton Room B | Unknown | The interactive touch screen does not have any sound or tactile components. Therefore, a visually impaired person would not be able to access the information provided by the kiosk. | §707 | Controls to operate the kiosk must meet the requirements of §707.Audio instructions must be provided that guide the user through all the functions of the machine. Tactile instructions must be provided informing the user on the method of activating the audio instructions. | 3000 | No | 8
2627 | Lemhi Room | Unknown | The TV protrudes 15" into the circulation space at 65" above the floor. | §307.2 | Ensure the desk remains underneath the TV to provide cane detectability. | 0 | Yes | 0
2626 | Teton Room B | Unknown | The TVs protrude 11.5" and 9.5" into the circulation space at 56" and 59" above the floor. | §307.2 | Ensure that the desks and chairs remain underneath the TVs to provide cane detectability. | 0 | Yes | 0
2653 | Women’s Restroom | Unknown | The dispenser protrudes 5" into the circulation space at 33.75" above the floor. | §307.2 | Ensure that the garbage can remains underneath the dispenser and paper towel dispenser. | 0 | Yes | 0
2639 | Entire Facility | Unknown | There are no tactile signs identifying 17 permanent room. | §216.2, §703 | Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space.Install tactile signage on the latch side of the doorway at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. | 1700 | Yes | 3
2617 | Step Ahead Idaho | Unknown | There are no tactile signs identifying the three permanent rooms. | §216.2, §703 | Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space.Install tactile signage on the latch side of the doorway at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. | 300 | Yes | 3
2624 | Study Rooms | Unknown | There are no tactile signs identifying three permanent rooms. | §216.2, §703 | Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space.Install tactile signage on the latch side of the doorway at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. | 300 | Yes | 3
2634 | Family Restroom | Unknown | The sharps container protrudes 4.75" into the circulation space at 41" above the floor. | §307.2 | Recess the sharps container so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
2671 | Main Entrance | Unknown | The paper towel dispenser protrudes 9" into the circulation space at 54.5" above the floor. | §307.2 | Recess the paper towel dispenser so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
2656 | Men’s Restroom | Unknown | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
2661 | Men’s Restroom | Unknown | The toilet paper dispenser is located out of the accessible reach range at 13" in front of the toilet. | §604.7 | The outlet of the dispenser shall be 15” minimum and 48” maximum above the floor and shall not be located behind.Remount the toilet paper dispenser to 7” minimum and 9” maximum in front of the water closet measured to the centerline of the dispenser. | 100 | Yes | 5
2663 | Men’s Restroom | Unknown | The sharps container protrudes 4.75" into the circulation space at 41" above the floor. | §307.2 | Recess the sharps container so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
2665 | Men’s Restroom | Unknown | The paper towel dispenser protrudes 8.5" into the circulation space at 48" above the floor. | §307.2 | Recess the paper towel dispenser so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
2667 | Reference Desk | Unknown | The TV protrudes 7.75" into the circulation space at 59" above the floor. | §307.2 | Recess the TV so it protrudes a maximum of 4", raise it so the bottom edge is 80" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
2668 | Reference Desk | Unknown | The AED protrudes 6" into the circulation space at 44" above the floor. | §307.2 | Recess the AED so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
2637 | Staff Area | Unknown | The MSDS protrudes 5" into the circulation space at 37" above the floor. | §307.2 | Recess the MSDS so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
2640 | Staff Area | Unknown | The fire extinguisher protrudes 4.25" into the circulation space at 37.5" above the floor. | §307.2 | Recess the fire extinguisher so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
2643 | Staff Area | Unknown | The first aid kit protrudes 6.5" into the circulation space at 50" above the floor. | §307.2 | Recess the first aid kit so it protrudes a maximum of 4" or place a cane detectable object beneath it. | 100 | Yes | 5
2638 | Staff Area | Unknown | The electrical box protrudes 6.25" into the circulation space at 33.75" above the floor. | §307.2 | Recess the electrical box so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 500 | Yes | 5
2623 | Step Ahead Idaho Restroom | Unknown | The paper towel dispenser protrudes 9" into the circulation space at 46" above the floor. | §307.2 | Recess the paper towel dispenser so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
2645 | Women’s Restroom | Unknown | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
2649 | Women’s Restroom | Unknown | The toilet paper dispenser is located out of the accessible reach range at 13" in front of the toilet. | §604.7 | The outlet of the dispenser shall be 15” minimum and 48” maximum above the floor and shall not be located behind.Remount the toilet paper dispenser to 7” minimum and 9” maximum in front of the water closet measured to the centerline of the dispenser. | 100 | Yes | 5
2650 | Women’s Restroom | Unknown | The space between the grab bar and the garbage can is 4". | §609.3 | Relocate the garbage can to a location that is at least a distance of 12" or greater above the top of the grab bar. Ensure that the garbage can is not greater than 48" above the floor. | 100 | Yes | 5
2651 | Women’s Restroom | Unknown | The sharps container protrudes 4.75" into the circulation space at 41" above the floor. | §307.2 | Recess the sharps container so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
2647 | Women’s Restroom | Unknown | The side grab bar is located 11" from the rear wall. | §604.5.1 | Remount the side grab bar 12" maximum from the rear wall and extending 54" minimum from the rear wall. | 500 | Yes | 5
2655 | Storage | Unknown | The tactile sign identifying the room is not in the correct location. | §703.4 | Reinstall the sign on the latch side of the door at 48" minimum above the floor measured from the baseline of the lowest character and 60" maximum measured from the baseline of the highest character. | 100 | Yes | 6
2664 | Men’s Restroom | Unknown | The mirrors are too high to be accessible at 41" above the floor. | §603.3 | Lower the mirror its bottom edge is a maximum height of 40" above the floor. | 200 | Yes | 7
2652 | Women’s Restroom | Unknown | The mirror is too high to be accessible at 41" above the floor. | §603.3 | Lower the mirror its bottom edge is a maximum height of 40" above the floor. | 200 | Yes | 7
2613 | Book Return | Unknown | The book return is outside of the unobstructed forward reach range at 50" above the floor. | §308.2.1 | Or add a secondary lower book drop at the same location. Lower the book return by 2" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
2635 | Family Restroom | Unknown | The hooks are outside of the unobstructed forward reach range at 62.5" above the floor. | §308.2.1 | Or install a secondary lower coat hook. Lower the hooks by 14.5" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
2636 | Family Restroom | Unknown | The paper towel dispenser is outside of the unobstructed forward reach range at 49.5" above the floor. | §308.2.1 | Lower the paper towel dispenser by 1.5" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
2629 | Lemhi Room | Unknown | The paper towel dispensers are outside of the obstructed forward reach range at 49.5" above the floor. | §308.2.2 | Lower the paper towel dispenser by 1.5" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
2644 | New Book Shelf | Unknown | The top shelf is outside of the unobstructed forward reach range at 63" above the floor. | §308.2.1 | Ensure that the library has a policy that provides assistance to employees and volunteers reaching for shelves that are located beyond 48” above the floor. | 100 | Yes | 8
2642 | Staff Area | Unknown | The paper towel dispensers are outside of the obstructed forward reach range at 52" above the floor. | §308.2.2 | Lower the paper towel dispenser by 8" to meet the accessible reach range of 15" minimum and 44" maximum above the floor. | 100 | Yes | 8
2616 | Step Ahead Idaho | Unknown | The top two rows of the paper holders are outside of the unobstructed forward reach range. | §308.2.1 | Lower the paper holders to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 200 | Yes | 8
2654 | Women’s Restroom | Unknown | The paper towel dispenser is outside of the unobstructed forward reach range at 49" above the floor. | §308.2.1 | Ensure that the garbage can remains underneath the paper towel dispenser at all times to provide cane detectability. Lower the paper towel dispenser by 1" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
2674 | Parking | Unknown | The accessible parking signs are 50" and 48" above the ground. The signs are also crooked. | §502.6 | Remount the accessible parking signs at each accessible space at a minimum height of 60" above the ground. | 400 | Yes | 9
High (1-4) | 10300
Medium (5-7) | 13100
Low (8-10) | 12300
Total | 35700
Quick Fix | 6700