## Capitol Library
Caption: Main Library! ADA assessment findings, recommendations for remediation, and associated costs.
ID | FACILITY | LOCATION | BUILT BEFORE ADA | VIOLATIONS | 2010 ADA CODE | RECOMMENDATIONS | ESTIMATED COST | QUICK FIX | PRIORITY SCORE
1258 | Capitol Library | Crosswalk by Book Returns | Yes | The pedestrian push button is located 43.5" above the floor. There is a step up adjacent to a ramped surface. | §405 | The reach range is accessible, however, for purposes of achieving greater accessibility, relocate the pedestrian push button to be adjacent to a level area. If the accessible parking space is relocated, this improvement is not required unless requested by an employee with a disability. | 0 | Yes | 8
1086 | Capitol Library | 1st Floor Hays Auditorium Women's Restroom | Yes | The sharps container protrudes 4.75" into the circulation path at 38" above the floor. | §307.2 | Recess the sharps container so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 10
1087 | Capitol Library | 1st Floor Hays Auditorium Women's Restroom | Yes | The dispenser protrudes 5.75" into the circulation path at 35" above the floor. | §307.2 | Recess the dispenser so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 10
1095 | Capitol Library | 1st Floor Youth Services Staff Workroom | Yes | The paper towel dispenser protrudes 9" into the circulation path at 40" above the floor. | §307.2 | Recess the dispenser so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 10
1105 | Capitol Library | 1st Floor Mail Room | Yes | The hangers are outside of the unobstructed forward reach range at 64" above the floor. | §308.2.1 | Lower the hangers by 16" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. Or add a secondary lower railing located within the accessible reach range. | 100 | Yes | 8
1121 | Capitol Library | 3rd Floor Women's Restroom | Yes | The hook is outside of the unobstructed forward reach range at 63" above the floor. | §308.2.1 | Lower the hook by 15" to meet the accessible reach range of 48" maximum above the floor. | 100 | Yes | 8
1131 | Capitol Library | 3rd Floor All Users Restroom | Yes | The hooks are outside of the obstructed forward reach range at 64" above the floor. | §308.2.2 | Lower the hooks by 16" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
1146 | Capitol Library | 3rd Floor All Users Restroom | Yes | The hooks are outside of the unobstructed forward reach range at 52" above the floor. | §308.2.1 | Lower the hooks by 4" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
1161 | Capitol Library | 4th Floor Kitchen | Yes | The paper towel dispenser is outside of the obstructed forward reach range at 58" above the floor. | §308.2.2 | Lower the paper towel dispenser by 10" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
1168 | Capitol Library | 4th Floor Women's Ambulatory Restroom | Yes | The hook is outside of the unobstructed forward reach range at 69" above the floor. | §308.2.1 | Lower the hook by 21" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
1173 | Capitol Library | 4th Floor Women's Ambulatory Restroom | Yes | The hook is outside of the unobstructed forward reach range at 50.75" above the floor. | §308.2.1 | Lower the hook by 2.75" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
1181 | Capitol Library | 2nd Floor Men's Restroom | Yes | The hooks are outside of the unobstructed forward reach range at 63.5" above the floor. | §308.2.1 | Lower the hooks by 15.5" or install a secondary lower hook to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
1188 | Capitol Library | 4th Floor Staff Break Room Vending Machine | Yes | The payment controls on the vending machine are outside of the unobstructed forward reach range at 52" above the floor. | §308.2.1 | Replace the vending machine with one that has controls located within the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
1226 | Capitol Library | 3rd Floor Comments Box | Yes | The comments box is outside of the obstructed forward reach range at 58" above the floor. | §308.2.2 | Lower the comments box by 10" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 100 | Yes | 8
1245 | Capitol Library | SW of the Library Building | Yes | One parking space is missing the signage identifying the accessible parking spaces. The parking space is located near Idaho Anne Frank Human Rights Memorial. | §502.6 | Install an accessible parking sign at each accessible space at a minimum height of 60" above the ground. | 100 | Yes | 9
1249 | Capitol Library | SW of the Library Building | Yes | The accessible parking sign is 56.5" above the ground. The parking space is located by Idaho Anne Frank Human Rights Memorial. | §502.6 | Remount the accessible parking sign at the accessible space at a minimum height of 60" above the ground. | 100 | Yes | 9
1262 | Capitol Library | Parking by Book Returns | Yes | The sign is 29.5" above the ground. | §502.6 | Remount the accessible parking sign at each accessible space at a minimum height of 60" above the ground. | 100 | Yes | 9
1079 | Capitol Library | 1st Floor Book Return | Yes | The shelf protrudes 8" into the circulation space at 28" above the floor. | §307.2 | Lower the shelf by 1" to 27" maximum above the floor, or provide cane detectability by placing an object underneath both ends of the counter. | 100 | Yes | 5
1080 | Capitol Library | 1st Floor Lobby | Yes | The charging station protrudes 4.5" into the circulation space at 38" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by recessing it or provide cane detectability by placing an object underneath. | 100 | Yes | 5
1081 | Capitol Library | 1st Floor Lobby | Yes | The fire extinguisher protrudes 6" into the circulation space at 30.5" above the floor. | §307.2 | Recess the fire extinguisher so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 5
1083 | Capitol Library | 1st Floor Hays Auditorium Women's Restroom | Yes | The toilet paper dispenser is located 4.5" above the side grab bar. | §609.3 | Relocate the toilet paper dispenser so that the bottom edge is at a location that is at least 12" or greater above the grab bar. Ensure that the center of the toilet paper dispenser is located 7" minimum to 9" maximum in front of the toilet and a maximum height of 48" above the floor. | 100 | Yes | 5
1085 | Capitol Library | 1st Floor Hays Auditorium Women's Restroom | Yes | The toilet seat cover dispenser is located 2.75" above the rear grab bar. | §609.3 | Relocate the toilet seat cover dispenser so that the bottom edge is at a location that is at least 12" or greater above the grab bar. Ensure that the dispenser is at a maximum height of 48" above the floor. | 100 | Yes | 5
1091 | Capitol Library | 1st Floor Youth Services Girl's Restroom | Yes | The mirror is located at 48" above the floor, too high to be accessible. | §603.3 | Lower the mirror so the bottom edge is a maximum height of 40" above the floor. | 100 | Yes | 7
1092 | Capitol Library | 1st Floor Youth Services Girl's Restroom | Yes | The dispenser protrudes 5.5" into the circulation space at 31" above the floor. | §307.2 | Recess the dispenser so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 5
1093 | Capitol Library | 1st Floor Youth Services Girl's Restroom | Yes | The pipes under the sink are not covered. | §606.5 | Wrap the pipes beneath the sink with soft protective wrap or plastic. | 100 | Yes | 7
1098 | Capitol Library | 1st Floor Women's Restroom | Yes | The toilet paper dispenser is 5" in front of the toilet. | §604.7 | Remount the toilet paper dispenser so that its center is located 7" minimum to 9" maximum in front of the toilet. Ensure that the height is within the accessible reach range of 15" minimum to 48" maximum above the floor. If mounted above the grab bar, ensure that the bottom edge of the dispenser at least 12" above the grab bar. | 100 | Yes | 5
1099 | Capitol Library | 1st Floor Women's Restroom | Yes | The sharps dispenser protrudes 4.75" into the circulation space at 45" above the floor. | §307.2 | Recess the dispenser so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 5
1100 | Capitol Library | 1st Floor Women's Restroom | Yes | The dispenser protrudes 5.75" into the circulation space at 30" above the floor. | §307.2 | Recess the dispenser so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 5
1102 | Capitol Library | 1st Floor Deliveries Garage | Yes | The fire extinguisher protrudes 4.5" into the circulation space at 28.5" above the floor. | §307.2 | Recess the fire extinguisher so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 7
1103 | Capitol Library | 1st Floor ATS | Yes | The shelf protrudes 6.5" into the circulation space at 45" above the floor. | §307.2 | Reduce the shelf protrusion depth to a maximum of 4” or lower it so the bottom edge is 27" maximum above the floor, or remove it. | 100 | Yes | 5
1106 | Capitol Library | 1st Floor Mail Room | Yes | The paper towel dispenser is outside of the unobstructed forward reach range at 53" above the floor. The paper towel dispenser protrudes 9" into the circulation space at 53" above the floor. | §307.2, §308.2.1 | Lower the paper towel dispenser by 5" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. Recess the dispenser so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 5
1109 | Capitol Library | 2nd Floor Women's Ambulatory Restroom | Yes | The space between the grab bar and the toilet paper dispenser is 5". | §609.3 | Remount the toilet paper dispenser so that its center is located 7” minimum to 9” maximum in front of the toilet. The bottom edge of the dispenser shall be at least 12" above the side grab bar. Ensure that the height is within the accessible reach range of 15” minimum to 48” maximum above the floor. | 100 | Yes | 5
1112 | Capitol Library | 2nd Floor Women's Restroom | Yes | The paper towel dispenser is outside of the unobstructed forward reach range at 49" above the floor. The paper towel dispenser protrudes 8.5" into the circulation space at 49" above the floor. | §307.2, §308.2.1 | Lower the paper towel dispenser by 1" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. Ensure that the trash can underneath the paper towel dispenser is always there to provide cane detectability. | 100 | Yes | 5
1113 | Capitol Library | 2nd Floor TV at Philosophy and Psychology Bookshelves | Yes | The TV protrudes 5" into the circulation space. | §307.2 | Recess the TV to reduce the protrusion depth to a maximum of 4" or lower it so that the bottom edge is at a maximum height of 27". | 100 | Yes | 5
1116 | Capitol Library | 3rd Floor Women's Restroom | Yes | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per ADA requirements. | 100 | Yes | 5
1118 | Capitol Library | 3rd Floor Women's Restroom | Yes | The space between the grab bar and the toilet paper dispenser is 3.5". | §609.3 | Remount the toilet paper dispenser so that its center is located 7” minimum to 9” maximum in front of the toilet. The bottom edge of the dispenser shall be at a maximum height of 12" above the grab bar. Ensure that the height is within the accessible reach range of 15” minimum to 48” maximum above the floor. | 100 | Yes | 5
1120 | Capitol Library | 3rd Floor Women's Restroom | Yes | The toilet paper dispenser lines up with the rim of the toilet which is not an accessible position. | §604.7 | Remount the toilet paper dispenser so that its center is located 7" minimum to 9" maximum in front of the toilet. The bottom edge of the dispenser shall be at a maximum height of 12” above the grab bar. Ensure that the height is within the accessible reach range of 15” minimum to 48” maximum above the floor. | 100 | Yes | 5
1122 | Capitol Library | 3rd Floor Women's Restroom | Yes | The space between the grab bar and the shelf is 3.75". | §609.3 | <div>Relocate the shelf to a location that is at least 12" or greater away from the top of the grab bar. Ensure that the shelf is located at a height not exceeding 48" above the floor. | 100 | Yes | 5
1123 | Capitol Library | 3rd Floor Women's Restroom | Yes | The sharps dispenser protrudes 4.75" into the circulation space at 43" above the floor. | §307.2 | Recess the dispenser so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 5
1125 | Capitol Library | 3rd Floor Women's Restroom | Yes | The dispenser protrudes 6"into the circulation space at 42" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. or lower the dispenser to a height not exceeding 27" above the floor. | 100 | Yes | 5
1136 | Capitol Library | 3rd Floor All Users Restroom | Yes | The toilet paper dispenser is 13" in front of the toilet. | §604.7 | Remount the toilet paper dispenser so that it is located 7" minimum to 9" maximum in front of the toilet. Ensure that the height is within the accessible reach range of 15" minimum to 48" maximum above the floor. If mounted above the side grab bar, the bottom edge of the dispenser shall be at a maximum height of 12” above the grab bar. | 100 | Yes | 5
1137 | Capitol Library | 3rd Floor All Users Restroom | Yes | The pipes under the sink are not covered. | §606.5 | Wrap the pipes beneath the sink with soft protective wrap or plastic. | 100 | Yes | 7
1138 | Capitol Library | 3rd Floor All Users Restroom | Yes | The shelf protrudes 8" into the circulation space at 62.25" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. | 100 | Yes | 5
1145 | Capitol Library | 3rd Floor All Users Restroom | Yes | The shelf protrudes 8" into the circulation space at 57.5" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. or lower the shelf to a height not exceeding 27" above the floor. | 100 | Yes | 5
1151 | Capitol Library | 3rd Floor All Users Restroom | Yes | The pipes under the sink are not covered. | §606.5 | Wrap the pipes beneath the sink with soft protective wrap or plastic. | 100 | Yes | 7
1156 | Capitol Library | 3rd Floor Reference Desk | Yes | The AED protrudes 6" into the circulation path at 46" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. | 100 | Yes | 5
1157 | Capitol Library | 3rd Floor Reference Desk | Yes | The paper towel dispenser protrudes 8" into the circulation space at 43" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. or lower the dispenser to a height not exceeding 27" above the floor. | 100 | Yes | 5
1160 | Capitol Library | 4th Floor Kitchen | Yes | The cabinet protrudes 12" into the circulation space at 46" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. | 100 | Yes | 5
1163 | Capitol Library | 4th Floor Women's Ambulatory Restroom | Yes | The door to the accessible water closet is not self closing. Either self-closing hinges are not installed on the door or if installed, they are defective. | §604.8.1.2 | Install or reinstall self-closing hinges on the door to ensure that the door is self-closing per the ADA requirements. | 100 | Yes | 5
1172 | Capitol Library | 4th Floor Women's Ambulatory Restroom | Yes | The dispenser protrudes 5.75" into the circulation space at 39.25" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. | 100 | Yes | 5
1174 | Capitol Library | 4th Floor Women's Ambulatory Restroom | Yes | The shelf is outside of the unobstructed forward reach range at 64.75" above the floor. The shelf protrudes 7" into the circulation space at 64.75" above the floor. | §307.2, §308.2.1 | Lower the shelf by 16.75" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. | 100 | Yes | 5
1183 | Capitol Library | 3rd Floor Reference Desk | Yes | The paper towel dispenser protrudes 9.5" into the circulation space at 43" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. | 100 | Yes | 5
1189 | Capitol Library | Learning Center | Yes | The fire extinguisher protrudes 6.5" into the circulation space at 39" above the floor. | §307.2 | The extinguisher is not located in an accessible path, however, for purposes of achieving greater accessibility and Human Centric Design, recess the fire extinguisher so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 100 | Yes | 5
1202 | Capitol Library | 1st Floor Youth Services Boy's Restroom | Yes | The pipes under the sink are not covered. | §606.5 | Wrap the pipes beneath the sink with soft protective wrap or plastic. | 100 | Yes | 7
1207 | Capitol Library | 1st Floor Men's Restroom | Yes | There is no door handle on the inside of the stall door. | §309.4 | Add a door handle to allow users to pull open the door. Ensure that the handle can be operated with a closed fist and without twisting the wrist. | 100 | Yes | 7
1214 | Capitol Library | 2nd Floor Men's Restroom | Yes | The space between the grab bar and toilet paper dispenser is 4". | §609.3 | Relocate the toilet paper dispenser to a location that is at least a distance of 12" or greater away from the grab bar. Ensure that the dispenser is at a height not exceeding 48" above the ground. The center of the toilet paper dispenser shall be located 7" minimum to 9" maximum in front of the toilet. | 100 | Yes | 5
1221 | Capitol Library | 3rd Floor Men's Restroom | Yes | The space between the side grab bar and the toilet paper dispenser is 3". | §609.3 | Relocate the toilet paper dispenser to a location that is at least a distance of 12" or greater away from the grab bar. Ensure that the dispenser is at a height not exceeding 48" above the ground. The center of the toilet paper dispenser shall be located 7" minimum to 9" maximum in front of the toilet. | 100 | Yes | 5
1224 | Capitol Library | 3rd Floor Men's Restroom | Yes | The paper towel dispenser protrudes 10" into the circulation space. | §307.2 | The dispenser is not located in an accessible path, however, for purposes of achieving greater accessibility and Human Centric Design, recess the dispenser so it protrudes a maximum of 4". Lower it so the bottom edge is 27" maximum above the floor, or ensure that the trash can is always under the dispenser to provide cane detectability. | 100 | Yes | 5
1232 | Capitol Library | 4th Floor Men's Restroom | Yes | The toilet paper dispenser is not located in an accessible position. | §604.7 | Remount the toilet paper dispenser so that it is located 7" minimum to 9" maximum in front of the toilet. Ensure that the height is within the accessible reach range of 15" minimum to 48" maximum above the floor. If mounted above the side grab bar, the bottom edge of the dispenser shall be 12" maximum above the grab bar. | 100 | Yes | 5
1238 | Capitol Library | 4th Floor Men's Restroom | Yes | The tactile sign identifying the room is not in the correct location. | §703.4 | Reinstall the sign on the latch side of the door at 48" minimum above the floor measured from the baseline of the lowest character and 60" maximum measured from the baseline of the highest character. | 100 | Yes | 6
1252 | Capitol Library | Main Entrance | Yes | There is not adequate clear floor space to access the push button. | §305.3 | Relocate the garbage can to ensure that a minimum clear and level floor space of 30"x48" is available by the push button. | 100 | Yes | 5
1190 | Capitol Library | 4th Floor Accounting Area | Yes | The fire extinguisher protrudes 5" into the circulation space at 29.5" above the floor. | §307.2 | <div>Recess the fire extinguisher so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
1211 | Capitol Library | 1st Floor ATS | Yes | The first aid box protrudes 5.5" into the circulation space. | §307.2 | Recess the box so it protrudes a maximum of 4", lower it so the bottom edge is 27" maximum above the floor, or place a cane detectable object beneath it. | 100 | Yes | 5
1233 | Capitol Library | 4th Floor Men's Restroom | Yes | The toilet seat cover dispenser and coat hook are outside of the unobstructed forward reach range at 54" and 57" above the floor. | §308.2.1 | Lower the toilet seat cover dispenser by 6" and the coat hook by 9" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. | 200 | Yes | 8
1101 | Capitol Library | 1st Floor Deliveries Garage | Yes | The fire extinguisher protrudes 5" into the circulation space at 29" above the floor. The fire extinguisher sign protrudes 4.5" into the circulation space at 70" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. or lower the extinguishers to a height not exceeding 27” above the floor. | 200 | Yes | 5
1111 | Capitol Library | 2nd Floor Women's Restroom | Yes | The tampon dispenser protrudes 5.5" into the circulation space at 30" above the floor. The sharps dispenser protrudes 4.75" at 44.5" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. Or lower the dispensers to a height not exceeding 27" above the floor. | 200 | Yes | 5
1115 | Capitol Library | 2nd Floor TVs | Yes | The TVs protrude 5" into the circulation space at 66" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. | 200 | Yes | 5
1152 | Capitol Library | 3rd Floor All Users Restroom | Yes | The shelf is outside of the unobstructed forward reach range at 63" above the floor. The shelf protrudes 8" into the circulation space at 63" above the floor. The dispenser protrudes 6" into the circulation space at 43.5" above the floor. | §307.2, §308.2.1 | Lower the shelf by 15" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. | 200 | Yes | 5
1170 | Capitol Library | 4th Floor Women's Ambulatory Restroom | Yes | The pipes under the sinks are not covered. | §606.5 | Wrap the pipes beneath the sinks with soft protective wrap or plastic. | 200 | Yes | 7
1171 | Capitol Library | 4th Floor Women's Ambulatory Restroom | Yes | The mirrors are too high to be accessible at 52" above the floor. | §603.3 | Lower the mirrors so the bottom edge is at a maximum height of 40" above the floor. | 200 | Yes | 7
1196 | Capitol Library | 1st Floor Hays Auditorium Men's Restroom | Yes | The toilet paper dispenser is located behind the rim of the toilet. The space between the grab bar and the toilet paper dispenser and the toilet seat covers is 4". | §609.3, §604.7 | Remount the toilet paper dispenser so that it is located 7" minimum to 9" maximum in front of the toilet. Ensure that the height is within the accessible reach range of 15" minimum to 48" maximum above the floor. Relocate the toilet paper and seat cover dispensers to a location that is at least a distance of 12" or greater above the grab bar. | 200 | Yes | 5
1209 | Capitol Library | 1st Floor Men's Restroom | Yes | The space between the grab bar and the toilet paper dispenser and toilet seat covers is 3". | §609.3 | Relocate the toilet paper dispenser and toilet seat covers to a location that is at least a distance of 12" or greater above the grab bar. | 200 | Yes | 5
1215 | Capitol Library | 2nd Floor Men's Restroom | Yes | The shelf is outside of the unobstructed forward reach range at 63" above the floor. The paper towel dispenser protrudes 10" into the circulation space. The shelf protrudes 12" into the circulation space at 63" above the floor. | §307.2, §308.2.1 | Lower the shelf by 15" to meet the accessible reach range of 15" minimum and 48" maximum above the floor. The objects are not located in an accessible path, however, for purposes of achieving greater accessibility and Human Centric Design, lower them so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath them. | 200 | Yes | 5
1266 | Capitol Library | Parking | Yes | The signage identifying the accessible parking spaces is 29.5" and 39.5" above the ground. | §502.6 | Remount the accessible parking sign at each accessible space at a minimum height of 60" above the ground. | 300 | Yes | 9
1182 | Capitol Library | 2nd Floor Paper Towel Dispensers | Yes | There are three paper towel dispensers protruding 9" into the circulation space at heights ranging from 44" to 49.5" above the floor. | §307.2 | Reduce the protrusion depth to a maximum of 4” by relocating it or provide cane detectability by placing an object underneath. | 300 | Yes | 5
1201 | Capitol Library | 1st Floor Youth Services Boy's Restroom | Yes | The mirror is too high to be accessible at 49" above the floor. The paper towel dispenser is outside of the unobstructed children's forward reach range at 45" above the floor. | §308.1, §603.3 | Lower the mirror to the maximum height of 40" above the floor. Therefore relocate the soap dispenser to the sidewall at a maximum height of 44" above the floor. Lower the paper towel dispenser to be between 16" and 44" above the floor. | 300 | Yes | 5
1236 | Capitol Library | 4th Floor Men's Restroom | Yes | The mirrors are too high to be accessible at 52" above the floor. | §603.3 | Lower the mirrors to the maximum height of 40" above the floor. | 300 | Yes | 7
1237 | Capitol Library | 4th Floor Men's Restroom | Yes | The pipes under the sink are not covered. | §606.5 | Wrap the pipes beneath the sink with soft protective wrap or plastic. | 300 | Yes | 7
1108 | Capitol Library | 2nd Floor Women's Ambulatory Restroom | Yes | The side grab bars are 33" long. | §604.5.1 | Replace the side grab bar with one that is a minimum of 42" long minimum, located 12" maximum from the rear wall and extending 54" from the rear wall. | 500 | Yes | 5
1127 | Capitol Library | 3rd Floor All Users Restroom | Yes | The shower spray unit is fixed. | §607.6 | Install a new shower spray unit that has a 59" long minimum hose to be used both as a fixed-position shower head and as a hand-held shower. | 500 | Yes | 6
1129 | Capitol Library | 3rd Floor All Users Restroom | Yes | The shower grab bar is installed at 42.5" above the ground. | §609.4 | Lower the grab bar to a minimum height of 33” and 36” maximum above the ground measured to the top of gripping surface. | 500 | Yes | 5
1130 | Capitol Library | 3rd Floor All Users Restroom | Yes | The bench is located 16" above the floor and 11" deep. | §903.3 | Install a new bench that is 20" to 24" inches deep. | 500 | Yes | 5
1142 | Capitol Library | 3rd Floor All Users Restroom | Yes | The grab bar is 43" above the floor. | §609.4 | Lower the grab bar to a minimum height of 33” and 36” maximum above the ground measured to the top of gripping surface. | 500 | Yes | 5
1144 | Capitol Library | 3rd Floor All Users Restroom | Yes | The bench is not deep or long enough at 17" and 11" wide. | §903.3 | Install a new bench that is at least 42" long and 20" to 24" inches deep. | 500 | Yes | 5
1198 | Capitol Library | 1st Floor Hays Auditorium Men's Restroom | Yes | The rear grab bar is located 10.5" to the center of the toilet. | §604.5.2 | Remount the rear grab bar to extend from the centerline of the water closet 12" minimum on one side and 24" minimum on the other. | 500 | Yes | 5
1210 | Capitol Library | 1st Floor Men's Restroom | Yes | The accessible water closet does not have a vertical grab bar per Idaho Statues. | ICC A117.1 §604.5.1 | Install an 18" long (minimum) vertical grab bar on the side wall. The grab bar shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. The centerline of the vertical grab bar shall be located 39" minimum and 41" maximum from the real wall. | 500 | Yes | 5
1177 | Capitol Library | 1st Floor Hays Auditorium | Yes | The dining and work surface counter is 36" above the floor. | §902.3 | A portion of the dining and work surface must be no higher than 34” above the ground. | 1000 | No | 8
1084 | Capitol Library | 1st Floor Hays Auditorium Women's Restroom | Yes | The toilet is 19" from the sidewall. | §604.2 | Reposition the toilet to be within 16" minimum and 18" maximum from the toilet's centerline. | 1000 | No | 5
1104 | Capitol Library | 1st Floor ATS | Yes | There is no knee clearance underneath the counter. | §306.3.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. | 1000 | No | 5
1128 | Capitol Library | 3rd Floor All Users Restroom | Yes | The shower does not have a seat. | §610.3.1, §610.3.2 | Install a permanent shower seat between 17" and 19" above the floor. The shower seat dimensions and shape shall comply with §610.3. | 1000 | No | 6
1134 | Capitol Library | 3rd Floor All Users Restroom | Yes | The side grab bar is 30" long. | §604.5.1 | Replace the side grab bar with one that is a minimum of 42" long minimum, located 12" maximum from the rear wall and extending 54" from the rear wall. Locate the side grab bar on the wall side. | 1000 | No | 5
1143 | Capitol Library | 3rd Floor All Users Restroom | Yes | The shower does not have a seat. | §610.3.1, §610.3.2 | Install a permanent shower seat between 17" and 19" above the floor. The shower seat dimensions and shape shall comply with §610.3. | 1000 | No | 6
1147 | Capitol Library | 3rd Floor All Users Restroom | Yes | There is no rear grab bar. The side grab bar is 29" long. | §604.5.1, §604.5.2 | Install a rear grab bar that is a minimum of 36" long minimum and extends from the centerline of the water closet 12" minimum on one side and 24" minimum on the other. Install a side grab bar on the wall side that is a minimum of 42" long minimum, located 12" maximum from the real wall and extending 54" from the rear wall. | 1000 | No | 5
1159 | Capitol Library | 4th Floor Kitchen | Yes | There is no knee clearance underneath the counter. The dining and work surface counter is 36" above the floor. | §902.3, §306.3.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. A portion of the dining and work surface must be no higher than 34” above the floor. | 1000 | No | 5
1194 | Capitol Library | 1st Floor Hays Auditorium Men's Restroom | Yes | The urinal height is 25" above the floor. | §605.2 | Lower the urinal so its rim is a maximum height 17" above the floor. | 1000 | No | 5
1208 | Capitol Library | 1st Floor Men's Restroom | Yes | The toilet is 19" from the sidewall. | §604.2 | Reposition the toilet to be within 16" minimum and 18" maximum from the sidewall. | 1000 | No | 5
1212 | Capitol Library | Stairwell | Yes | There are no handrails. | §505.2 | Install handrails at a minimum height of 34” and maximum of 38” above the ground. Make sure there are adequate handrail extensions both at the top and bottom of the handrail. Handrails shall extend 12" at the top of the stair flight, and at the bottom, they shall return to a wall, guard, or landing surface. | 1000 | No | 6
1218 | Capitol Library | 3rd Floor Admin Corner Office | Yes | There is no knee clearance underneath the counter. | §306.3.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. | 1000 | No | 5
1220 | Capitol Library | 3rd Floor Men's Restroom | Yes | The urinal rim is 24" above the floor. | §605.2 | Lower the urinal so the rim is a maximum height of 17" above the floor. | 1000 | No | 5
1230 | Capitol Library | 4th Floor Men's Restroom | Yes | The distance betwee the two hinged or pivoted doors is 36", which is lower than the 48" required. | §404.2.6 | Remove one of the doors to ensure adequate maneuvering clearance of 48" between the two doorways. | 1000 | No | 5
1231 | Capitol Library | 4th Floor Men's Restroom | Yes | The toilet compartment size is too small at 56" deep and 38" wide. | §604.8.1.1 | Combine the two non-accessible stalls into one 60" wide wheelchair accessible toilet stall, complying with §604.8. | 1000 | No | 7
1235 | Capitol Library | 4th Floor Men's Restroom | Yes | The urinals are 23" above the floor. | §605.2 | Lower at least one of the urinals to a maximum height of 17"above the floor. | 1000 | No | 5
1243 | Capitol Library | Book Return Crosswalk in Parking Lot | Yes | The crack in the pavement is 2.5" wide and 1.5" deep. | §303.2 | Resurface the pathway to reduce the change in level to less than 0.25". | 1000 | No | 5
1253 | Capitol Library | Main Entrance | Yes | Handrails extension are located in an area with a 3% running slope. | §505.10.1 | Extensions are required at the top and bottom of the ramp run. After a ramp run, there must be level landings with a maximum slope of 2%. Extend the handrails so that the handrail extensions are located in an area with slopes not exceeding 2%. The handrail extensions shall either return to a wall, guard, or the landing surface which extend at least 12" beyond the ramp run. | 1000 | No | 5
1158 | Capitol Library | 3rd Floor Reference Desk | Yes | The counter is 42" above the floor. | §904.4.1 | A portion of the service counter must be no higher than 36” above the floor for a horizontal distance of 36”. | 1000 | No | 4
1193 | Capitol Library | 1st Floor Hays Auditorium Men's Restroom | Yes | The paper towel dispenser is 10" deep and protrudeds 6" beyond the garbage can. | §307.2 | The dispenser is not located in an accessible path, however, for purposes of achieving greater accessibility and Human Centric Design, recess the dispenser so it protrudes a maximum of 4". Lower it so the bottom edge is 27" maximum above the floor, or place a cane-detectable object beneath it. | 1000 | No | 5
1200 | Capitol Library | 1st Floor Youth Services Boy's Restroom | Yes | The maneuvering clearance at the restroom door is not accessible. | §404.2.4 | Relocate the table to provide a maneuvering clearance 60" perpendicular to the door and 18" parallel to the door. | 1000 | No | 3
1268 | Capitol Library | Parking | Yes | There is a total of 143 spaces and only 3 spaces are designated as accessible. | §208.2 | Pave two additional accessible spaces 96" wide and 60" access aisle. Ensure that the slope is a maximum of 2% in all direction. | 1000 | No | 3
1204 | Capitol Library | 1st Floor Youth Services Staff Workroom | Yes | There is no knee clearance underneath the counter. The dining and work surface counter is 36" above the floor. | §902.3, §306.3.3 | Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. A portion of the dining and work surface must be no higher than 34” above the floor. | 1500 | No | 5
1175 | Capitol Library | Friends of the Library Storage | Yes | The shelves are too close together and there is not a clear width of 36" for wheelchairs to pass. The distances are 29" and 32". | §403.5.1 | Move the shelves to provide a minimum distance of 36" between the shelves. This is an employee work area and remediation is required only if requested by a qualified employee. Ensure that the library has a policy that provides assistance to employees and volunteers reaching for shelves that are located beyond 48” above the floor. | 2000 | No | 8
1088 | Capitol Library | 1st Floor Hays Auditorium | Yes | There is only one drinking fountain provided. | §211.2, §602.7 | Install an additional drinking fountain at a minimum spout height of 38" and maximum of 43" above the floor. | 2000 | No | 6
1090 | Capitol Library | 1st Floor Youth Services Girl's Restroom | Yes | The toilet compartment size is too small. | §604.8.1.1 | Combine the two non-accessible stalls into one 60" wide wheelchair accessible toilet stall. Add grab bars at a minimum height of 33" and 36" maximum above the floor. | 2000 | No | 7
1107 | Capitol Library | 1st Floor Women's Restroom | Yes | There is only one drinking fountain provided. | §211.2, §602.7 | Install an additional drinking fountain at a minimum spout height of 38" and maximum of 43" above the floor. | 2000 | No | 6
1133 | Capitol Library | 3rd Floor All Users Restroom | Yes | There is no rear grab bar. The side grab bar is 30" long. | §604.5.1, §604.5.2 | Install a rear grab bar that is a minimum of 36" long minimum and extends from the centerline of the water closet 12" minimum on one side and 24" minimum on the other. Replace the side grab bar with one that is a minimum of 42" long minimum, located 12" maximum from the rear wall and extending 54" from the rear wall. Locate the side grab bar on the wall side. | 2000 | No | 5
1155 | Capitol Library | 3rd Floor Drinking Fountain | Yes | There is only one drinking fountain provided at a spout height of 33" above the floor. | §211.2, §602.7 | Install an additional drinking fountain at a minimum spout height of 38" and maximum of 43" above the floor. | 2000 | No | 6
1162 | Capitol Library | 4th Floor Restrooms | Yes | There is only one drinking fountain provided at 36.5". | §211.2, §602.4, §703.4.2 | Lower the current drinking fountain to a maximum of 36" above the floor. Install an additional drinking fountain at a minimum height of 38" and maximum of 43" above the floor. Relocate the drinking fountain to prove a 18"x18" clear floor space in front of the restroom sign. | 2000 | No | 6
1165 | Capitol Library | 4th Floor Women's Ambulatory Restroom | Yes | The side grab bars are not long enough. | §604.5.1 | Replace the side grab bars with ones that are a minimum of 42" long minimum, located 12" maximum from the rear wall and extending 54" from the rear wall. | 2000 | No | 5
1178 | Capitol Library | 1st Floor Youth Services | Yes | There is only one drinking fountain provided. | §211.2, §602.7 | Install an additional drinking fountain at a minimum height of 38" and maximum of 43" above the floor. | 2000 | No | 6
1179 | Capitol Library | 1st Floor | Yes | There is a handrail on one side. Handrails do not extend at least 12" beyond the ramp run. The running slope of the ramp is 13.5%. | §405.2, §505.2, §505.10.1 | Install a handrail on the wall at a minimum height of 34” and maximum of 38” above the ground. Extend the ramp handrails 12” horizontally beyond the top and bottom of ramp run. Reconstruct the ramp to reduce the running slope to less than 8.3%. Provide a 60" level landing for every 30" of length. | 2000 | No | 5
1186 | Capitol Library | 3rd Floor Staff Break Room | Yes | The dining and work surface counter is 36" above the floor. There is no knee clearance underneath the counter. The suggestion box protrudes 6” into the circulation space at 39” above the floor. The shelf protrudes 19.5” into the circulation space at 41.75” above the floor. | §306.3.3, §902.3 | A portion of the dining and work surface must be no higher than 34” above the floor. Provide knee clearance underneath the counter at the sink that is a minimum of 11" deep at 9" above the floor and 8" deep at 27" above the floor. Lower the shelf and box so the bottom edge is 27” maximum above the floor, or place a cane detectable object beneath them. | 2000 | No | 5
1187 | Capitol Library | 3rd Floor Staff Break Room | Yes | There is only one drinking fountain provided. | §211.2, §602.7 | Install an additional drinking fountain at a minimum height of 38" and maximum of 43" above the floor. | 2000 | No | 6
1195 | Capitol Library | 1st Floor Hays Auditorium Men's Restroom | Yes | The toilet compartment is 53" wide. | §604.8.1.1 | Relocate partition to provide a 60" wide wheelchair accessible toilet stall, complying with §604.8. | 2000 | No | 7
1216 | Capitol Library | 2nd Floor Drinking Fountain | Yes | There is only one drinking fountain provided at a height of 32" above the floor. | §211.2, §602.7 | Install an additional drinking fountain at a minimum height of 38" and maximum of 43" above the floor. | 2000 | No | 6
1261 | Capitol Library | Parking by Book Returns | Yes | The accessible parking space has a 3.1% slope. | §502.4 | Resurface the parking space to reduce the slope to less than 2% in all directions. Relocate the accessible space to be located near the entrance. | 2000 | No | 3
1259 | Capitol Library | Curb Ramp by Book Returns | Yes | The running slope of the curb ramp is 11.6%. | §405.2 | Reconstruct the curb ramp to reduce the running slope to a maximum of 8.3%. if the accessible parking space is relocated, the is remediation will be required only if requested by a qualified employee. | 2500 | No | 7
1250 | Capitol Library | SW of the Library Building | Yes | The access aisle has a 3% cross slope. Parking by Idaho Anne Frank Human Rights Memorial. | §502.4 | Resurface the access aisle to reduce the slope to less than 2% in all directions. | 4000 | No | 3
1126 | Capitol Library | 3rd Floor All Users Restroom | Yes | There is a 5.25" step at the shower entrance, rendering the shower inaccessible. | §213.3.6 | Install at least one accessible shower complying with §607 or §608. | 5000 | No | 6
1169 | Capitol Library | 4th Floor Women's Ambulatory Restroom | Yes | The toilet compartment size is too small at 37.5" wide and 55.5" deep. | §604.8.1.1 | Combine the two non-accessible stalls into one 60" wide wheelchair accessible toilet stall, complying with §604.8. | 5000 | No | 7
1191 | Capitol Library | Entire Facility | Yes | There are 50 door knobs throughout the facility that require twisting of the wrist. | §309.4 | Replace the door knobs with lever handles that can be operated with a closed fist and without twisting the wrist. | 5000 | No | 7
1203 | Capitol Library | 1st Floor Youth Services Boy's Restroom | Yes | The toilet compartment size is too small. | §604.8.1.1 | Combine the two non-accessible stalls into one single use unisex 60" wide wheelchair accessible toilet stall, complying with §604.8. | 5000 | No | 7
1213 | Capitol Library | 2nd Floor Men's Restroom | Yes | The toilet compartment size is too small at 40" wide. | §604.8.1.1 | Combine the two non-accessible stalls into one 60" wide wheelchair accessible toilet stall, complying with §604.8. | 5000 | No | 7
1234 | Capitol Library | 4th Floor Men's Restroom | Yes | The toilet compartment size is too small as the stall is 31" wide and 34" deep. | §604.8.1.1 | Combine the two non-accessible stalls into one 60" wide wheelchair accessible toilet stall, complying with §604.8. | 5000 | No | 7
1241 | Capitol Library | Bike Parking | Yes | Due to the location of the bike rack in the accessible route, there is the possibility that the 36" clear width for wheelchairs to pass may be reduced based upon the placement of the bicycles. | §403.5.3 | Consider shifting the bike rack all the way to one side of the sidewalk to ensure that there is enough space. | 5000 | No | 5
4458 | Capitol Library | Restrooms | Yes | The accessible water closets do not have a vertical grab bars. | ICC A117.1 §604.5.1 | Install vertical grab bars with a minimum length of 18". The grab bars shall be mounted with the bottom located at 39" minimum and 41" maximum above the floor. The centerline of the vertical grab bars shall be located 39" minimum and 41" maximum from the real wall. | 5000 | No | 5
1205 | Capitol Library | 1st Floor Counters | Yes | The check out counter is 39.5" above the floor. | §904.4.1 | A portion of the service counter must be no higher than 36” above the floor for a horizontal distance of 36”. | 5000 | No | 4
1219 | Capitol Library | 3rd Floor Men's Restroom | Yes | The hallway width is 45.5" wide, providing inadequate maneuvering clearance in front of the door. | §404.2.4.1 (h) | Remove the hallway to provide a minimum of 48" maneuvering clearance in front of the door. In the meantime, provide signage directing users to the nearest accessible restroom. | 5000 | No | 3
1244 | Capitol Library | Employee Parking | Yes | There is no accessible parking spaces or an accessible route provided from the employee parking lot to the employee entrance. | §208.2, §206.2.1 | Ensure that the library has a policy that either allows qualified employees with disabilities to park in the patron lot or provide an accessible parking space for employees with disabilities upon request of accomodation. | 5000 | No | 3
1257 | Capitol Library | Curb Ramp by Book Returns | Yes | The curb ramp is not wide enough to provide access to wheelchairs and does not provide a level turning space at the top of the ramp. | §403.5.1, §405.7 | Reconstruct the curb ramp to provide a 36" wide accessible route. Pave a level landing with a minimum length of 60" and as wide as the ramp. The maximum slope shall be 2% in all directions. Ensure that the maximum running and cross slopes of the sidewalk are 5% and 2% respectively. | 5000 | No | 3
1263 | Capitol Library | Curbside Parking | Yes | The passenger loading zones have a 3.5% cross slope. The different colors of the curbside spaces may confuse the user. | §502.4 | Resurface the accessible passenger loading zones to reduce the slope to less than 2% in all directions. | 5000 | No | 3
1265 | Capitol Library | Parking | Yes | Portions of the parking spaces and access aisle have a 3% running slope and 3.5% cross slope. | §502.4 | Resurface the parking spaces and access aisle to reduce the slope to less than 2% in all directions. | 5000 | No | 3
1140 | Capitol Library | 3rd Floor All Users Restroom | Yes | There is a 5.25" step at the shower entrance and the spray unit is fixed. | §404.2.5, §607.6 | Reconstruct the entrance to reduce the threshold to a maximum og 1/2". Install a new shower spray unit that has a 59" long minimum hose to be used both as a fixed-position shower head and as a hand-held shower. | 6000 | No | 3
1217 | Capitol Library | 2nd Floor Aisle by Wall | Yes | The wall columns reduce the width of the aisles to 34" wide for over 24" in length. | §403.5.1 | Move the shelves to provide a minimum distance of 36” between the shelves. Ensure that the library has a policy that provides assistance to patrons reaching for shelves that are located beyond 48” above the floor. | 10000 | No | 5
1227 | Capitol Library | 4th Floor | Yes | Handrails are not continuous for the full length of the stairwell. There are no handrail extensions for the ramp. The handrails are flat and therefore do not have a compliant non-circular or circular cross section. | §505.10, §505.7.2, §505.3 | Extend the handrails to be continuous for the entire length of the stairwell. Extend the stairwell handrails 12” horizontally beyond the top and bottom of ramp runs. Install new handrails with a non-circular cross section diameter of 4" minimum and 6.25" maximum OR install new handrails with a circular cross section diameter of 1.25" minimum and 2" maximum. | 10000 | No | 5
1114 | Capitol Library | 2nd Floor Laptop Station | Yes | The interactive touch screen does not have any audio or tactile components. Therefore, a visually imparied person would not be able to access the laptop station. | §707 | Audio instructions must be provided that guide the user through all the functions of the machine. Tactile instructions must be provided informing the user on the method of activating the audio instructions. Controls to operate the laptop station must meet the requirements in §707. | 10000 | No | 2
1154 | Capitol Library | Entire Facility | Yes | There are no tactile signs identifying 110 permanent rooms. | §216.2, §703 | Install tactile signage on the latch side of the doorways at a height of 48” minimum to 60” maximum above the floor, identifying room by name or room number. Signs shall be Braille with raised lettering and should be placed on the wall in the center of an 18"x18" clear floor space. | 11000 | No | 3
1254 | Capitol Library | Main Entrance | Yes | Curvilinear ramps can create compound slopes that cannot meet the requirements for accessible routes. The landing is 58" long. | §405, §405.7.3 | It is recommended that the curvilinear ramp be redesigned in the future so as to not be curved if the running slope exceeds 5%. Expand the provided landing to ensure that the clear length is 60" long minimum to allow adequate turning space. | 20000 | No | 3
High (1-4) | 86000
Medium (5-7) | 119600
Low (8-10) | 5100
Total | 210700
Quick Fix | 13700