## Interface
City of Boise - Assured Water Supply - Water Demand Calculator Tool
for AWS Application B and Application C
2024-05-16
Instructions: This water demand calculator tool can be used to aid developers in calculating the water demand for their developments based on the number of customers (i.e water meters). To use this tool, simply input the number of customers (Residential or Commercial/Industrial) that will exist at full build-out of the proposed development. The water demand calculator tool will output the predicted water demand.
Projected Number of Residential Customers | 20
Residential ADD* | 6712.4 | gallons per day
Residential MDD** | 14901.528 | gallons per day
*Average Daily Demand
**Maximum Daily Demand
Projected Number of Commercial/Industrial Customers | 10
Commercial/Industrial ADD | 17000 | gallons per day
Commercial/Industrial MDD | 31280 | gallons per day
Total Development Average Day Water Demand (ADD) = | 23712.4 | gallons per day
Total Development Max Day Water Demand (MDD) = | 46181.528 | gallons per day
Legend
Input
Calculation
Output

## Calculations Sheet
(A) Residential Development
Parameter | Full Buildout of Service Area | From IMAP - Appendix A
Residential Use per Customer (kgal)
Residential Demands |  |  | 13 | kGal | Gal / Customer | Gal / Customer / Day
Projected No. of Residential Customers | 20 | 31 | Jan | 3.65 | 3650 | 117.7419
1Average Residential Demand Factor (gpd / customer) | 335.62 | 28 | Feb | 4.84 | 4840 | 172.8571
Total Projected ADD* (gpd) | 6712.4 | 31 | Mar | 3.77 | 3770 | 121.6129
1Peaking Factor | 2.22 | 30 | Apr | 4.53 | 4530 | 151
Total Projected MDD** (gpd) | 14901.528 | 31 | May | 4.83 | 4830 | 155.8065
*Average Daily Demand |  | 30 | Jun | 9.03 | 9030 | 301
**Maximum Daily Demand |  | 31 | Jul | 14.94 | 14940 | 481.9355
|  | 31 | Aug | 20.53 | 20530 | 662.2581
(B) Commercial and Industrial Development |  | 30 | Sep | 20.89 | 20890 | 696.3333
Parameter | Full Buildout of Service Area | 31 | Oct | 19.15 | 19150 | 617.7419
|  | 30 | Nov | 11.15 | 11150 | 371.6667
|  | 31 | Dec | 5.95 | 5950 | 191.9355
Commercial and Industrial Demands |  |  | avg month | 10.2717 |  | 336.8241
Projected No. of Commercial/Industrial Customers | 10 |  | peak month | 20.89
1Average Demand Factor (gpd / customer) | 1700 |  | PF (ADD to MMAD) | 2.0337
Total Projected ADD* (gpd) | 17000 |  | PF (MMAD to MDD) | 1.09
1Peaking Factor | 1.84 |  | Res PF | 2.2168
Total Projected MDD** (gpd) | 31280
Commercial Use per Customer (kgal)
|  |  | 13 | kGal | Gal / Customer | Gal / Customer / Day
Inputs |  | 31 | Jan | 33.1 | 33100 | 1067.7419
Calculations |  | 28 | Feb | 33.31 | 33310 | 1189.6429
Referenced Values |  | 31 | Mar | 33.45 | 33450 | 1079.0323
Outputs |  | 30 | Apr | 33.47 | 33470 | 1115.6667
|  | 31 | May | 33.31 | 33310 | 1074.5161
References |  | 30 | Jun | 44.02 | 44020 | 1467.3333
1Suez Water Idaho Inc.(2016) MASTER WATER PLAN FOR THE YEARS 2015 TO 2065. |  | 31 | Jul | 59.06 | 59060 | 1905.1613
|  | 31 | Aug | 86.63 | 86630 | 2794.5161
|  | 30 | Sep | 86.1 | 86100 | 2870
|  | 31 | Oct | 85.23 | 85230 | 2749.3548
|  | 30 | Nov | 54.16 | 54160 | 1805.3333
|  | 31 | Dec | 35.24 | 35240 | 1136.7742
|  |  | avg month | 51.4233 |  | 1687.9227
|  |  | peak month | 86.63
|  |  | PF (ADD to MMD) | 1.6846
|  |  | PF (MMAD to MDD) | 1.09
|  |  | Com PF | 1.8363

## Res & Comm Demand
Suez Water Idaho Inc. (2016) MASTER WATER PLAN FOR THE YEARS 2015 TO 2065. | Residential |  | Demand Per Customer Per Day | Commercial/Industrial |  | Demand Per Customer Per Day
| 120000 | 365 | 328.7671 | 619000 | 365 | 1695.8904
| 121000 | 365 | 331.5068 | 620000 | 365 | 1698.6301
| 122000 | 365 | 334.2466 | 621000 | 365 | 1701.3699
| 123000 | 365 | 336.9863 | 622000 | 365 | 1704.1096
| 124000 | 365 | 339.726 | 623000 | 365 | 1706.8493
| 125000 | 365 | 342.4658 | 624000 | 365 | 1709.589
|  | AVG: | 335.6164 |  | AVG: | 1700